                                    [image: image1]
[image: image2.jpg]El



[image: image3.png]B

W]




 H07V-K PVC电线                           HOOK-UP WIRE
[image: image4.png]PRODUCT DESCRIPTION



[image: image5.png]APPLICATION



                                                                                                              
	●额定温度：70℃
●额定电压：450V/750V
●参考标准：DIN 7724 (VDE)

●导体使用单支或绞合1.5-16mm2镀锡或裸铜
●PVC绝缘，符合ROHS环保标准
●绝缘厚度均匀、易裁线、易剥皮
	●Rated temperature：70℃
●Rated voltage：450V/750V
●Reference standard：DIN 7724 (VDE)
●Solid or stranded ,tinned or bare copper conductor 1.5-16mm2
●PVC insulation ,comply with ROHS environmental standard 
●Uniform insulation thickness to ensure easy stripping and cutting


[image: image6.png][

n




[image: image7.wmf]PVC Insulation 

PVC

绝缘

Conductor

 

导体


 ●用于一般电子、电器设备内部连接线，            ●For general purpose internal wiring of appliance.,

   电机、变压器和灯具引出线                        electronic equipments lead wires of motors.

                     

■印字 MARKING
   VDE     H07V-K  XX. mm2  70℃  450V/750V  CLEVER
■产品结构   CABLE CONSTRUCTION 
	型号
STYLE
	导体
CONDUCTOR
	绝缘
INSULATION
	包装长度
PACKAGING LENGTH
	最大导体电阻
MAX.COND.

RESISTANCE （Ω/km,20℃,DC）

	
	mm2
	 线数/线径

No./mm
	外径

DIA.

(mm)
	厚度

THICKNESS

（mm）
	外径

O.D.

(mm)
	英制

Ft/Coil
	公制

M/Coil
	

	H07V-K
	1.50
	30/0.25
	1.60
	0.70
	2.90
	1000
	305
	13.70

	
	2.50
	50/0.25
	2.00
	0.80
	3.60
	1000
	305
	8.21

	
	4.00
	56/0.30
	2.60
	0.80
	4.10
	1000
	305
	5.09

	
	6.00
	84/0.30
	3.20
	0.80
	4.60
	1000
	305
	3.39

	
	10.00
	80/0.40
	4.13
	1.00
	6.00
	500
	152.5
	1.88

	
	16.00
	126/0.40
	5.90
	1.00
	7.00
	500
	152.5
	1.72

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	


conductor tolerance 单支导体公差：+/-0.005mm, wire tolerance芯线外径公差：ＯＤ+/-0.10mm。

 以上仅供参考，详细规格按双方确认规格书为准

� EMBED  \* MERGEFORMAT ���








_1234567890.dwg

