File E124949

Project 99NK8996A

February 15, 2000

REPORT

ON

POWER CONVERSION EQUIPMENT

LG Industrial Systems Co., Ltd.

Chungnam Korea

Copyright  ©  2000 Underwriters Laboratories Inc.

Underwriters Laboratories Inc. authorizes the above named company to reproduce this Report provided it is reproduced in its entirety.

File E124949	Vol. 1	Sec. 8	Page 1	Issued:	2-15-00

and Report		Revised:	11-02-01

DESCRIPTION

PRODUCT COVERED:

*	AC adjustable speed drive controller inverter, Types SV; followed by 030, 037, 045, 055, 075, 090, 110, 132, 160, 220; followed by iH; followed by -4; followed by U; and may be followed by -DB.  Optionally, the inverter may be identified as Type RSi; followed by 040, 050, 060, 075, 100, 125, 150, 200, 250, 300; followed by -H; followed by -4; followed by -L; and may be followed by -DB.

GENERAL:

The products covered by this report are general purpose, insulated gate bipolar transistor (IGBT) AC motor controller, operating from a three-phase source of supply.  They are intended to control three-phase induction motor by means of a variable frequency, variable voltage output.

The units are intended for mounting within another enclosure suitable for the application, with forced filtered ventilation (as an open device), or for wall mounting an enclosed device with permanent connection to the supply source in a pollution degree 2 environment.

ENGINEERING CONSIDERATIONS:  (Not for Field Representative's Use)

Spacings - Spacings on Printed Wiring Boards were evaluated per UL 508C, Second Edition, Table 35.1.

File E124949	Vol. 1	Sec. 8	Page 1A	Issued:	2000-02-15

and Report		Revised:	2004-03-15

ELECTRICAL RATING:

Power Inputs and Outputs -

| LG Models | Corresponding Benshaw Models | HP |  | Input |  |  |  |  | Output |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | ## CT | VT | Vac | Phase | Hz | CT (Arms) | VT (Arms) | Vac | Phase | Hz | CT (Arms) | VT (Arms) |
| SV030iH-4U | RSi-040-H-4-L | 40 | 50 | 380 or 440 or 460 or 480 or 380~460 or 380~480 | 3 | 50-60 | 72 | 94 | 0~Vin | 3 | 0.5-400 | 61 | 80 |
| SV037iH-4U | RSi-050-H-4-L | 50 | 60 | 380 or 440 or 460 or 480 or 380~460 or 380~480 | 3 | 50-60 | 88 | 112 | 0~Vin | 3 | 0.5-400 | 75 | 96 |
| SV045iH-4U | RSi-060-H-4-L | 60 | 75 | 380 or 440 or 460 or 480 or 380~460 or 380~480 | 3 | 50-60 | 102 | 129 | 0~Vin | 3 | 0.5-400 | 91 | 115 |
| SV055iH-4U | RSi-075-H-4-L | 75 | 100 | 380 or 440 or 460 or 480 or 380~460 or 380~480 | 3 | 50-60 | 128 | 145 | 0~Vin | 3 | 0.5-400 | 110 | 125 |
| SV075iH-4U | RSi-100-H-4-L | 100 | 125 | 380 or 440 or 460 or 480 or 380~460 or 380~480 | 3 | 50-60 | 178 | 187 | 0~Vin | 3 | 0.5-400 | 152 | 160 |
| SV090iH-4U | RSi-125-H-4-L | 125 | 150 | 380 or 440 or 460 or 480 or 380~460 or 380~480 | 3 | 50-60 | 214 | 267 | 0~Vin | 3 | 0.5-400 | 183 | 228 |
| SV110iH-4U | RSi-150-H-4-L | 150 | 175/200 | 380 or 440 or 460 or 480 or 380~460 or 380~480 | 3 | 50-60 | 260 | 308 | 0~Vin | 3 | 0.5-400 | 223 | 264 |
| SV132iH-4U | RSi-200-H-4-L | 175/200 | 215/250 | 380 or 440 or 460 or 480 or 380~460 or 380~480 | 3 | 50-60 | 309 | 386 | 0~Vin | 3 | 0.5-400 | 264 | 330 |
| SV160iH-4U | RSi-250-H-4-L | 215/250 | 250/300 | 380 or 440 or 460 or 480 or 380~460 or 380~480 | 3 | 50-60 | 380 | 422 | 0~Vin | 3 | 0.5-400 | 325 | 361 |
| SV220iH-4U | RSi-300-H-4-L | 300 | 350 | 380 or 440 or 460 or 480 or 380~460 or 380~480 | 3 | 50-60 | 507 | 560 | 0~Vin | 3 | 0.5-400 | 432 | 477 |

Where CT = Constant Torque Rating, VT = Variable Torque Rating. Auxiliary Output - Terminals 1A, 1B, 2A, 2B-250 V ac, 1 A; 30 V dc, 1 A.  Fault Output - Terminals A, B, C (may also be labeled 30A, 30B,30C) - 250 V ac, 1 A; 30 V dc, 1 A.

All Remaining Control Circuit Terminals - Class 2 or Limited Voltage/Current, 24 V dc.  External Braking Unit/Resistor Terminals - Terminals P1, P2, N – 400 V dc, 200 A for 240 V drives; 800 V dc, 150 A for 480 V drives.

Short Circuit rating –

RSi-040-H-4-L - RSi - 250-H-4-L - 65 kA rms

RSi-300-H-4-L - 5 kA rms.

# Surrounding Air Ambient Rating – 45°C max.

# File E124949	Vol. 1	Sec. 8	Page 2	Issued:	2000-02-15

and Report		Revised:	2003-11-13

NOMENCLATURE:

The drives are designated:

| Rsi |  | 040 | - | H | - | 4 | - | L |  | DB |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| I |  | II |  | III |  | IV |  | V |  | VI |

I	Rsi - Ready-Start Inverter (Trade Name)

II	040 - Applicable Motor Capacity (40 HP Constant Torque)

050 - Applicable Motor Capacity (50 HP Constant Torque)

060 - Applicable Motor Capacity (60 HP Constant Torque)

075 - Applicable Motor Capacity (75 HP Constant Torque)

100 - Applicable Motor Capacity (100 HP Constant Torque)

125 - Applicable Motor Capacity (125 HP Constant Torque)

150 - Applicable Motor Capacity (150 HP Constant Torque)

200 - Applicable Motor Capacity (200 HP Constant Torque)

250 - Applicable Motor Capacity (250 HP Constant Torque)

300 - Applicable Motor Capacity (300 HP Constant Torque)

III	H - Series name of inverter (H - Series)

*	IV	2 - Represents Input Voltage Rating (200-240 V ac)

4 - Represents Input Voltage Rating (380-480 V ac)

V	L - Indicates UL Listed drive.

VI	DB - Optional - Dynamic Braking Chopper.

File E124949	Vol. 1	Sec. 8	Page 2A	Issued:	2000-02-15

and Report		Revised:	2003-11-13

NOMENCLATURE:

The drives are designated:

|  | SV |  | 030 |  | iH |  | -4 |  | U |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | I |  | II |  | III |  | IV |  | V |

I	SV - Starvert (Trade Name)

II	030 - Applicable Motor Capacity (40 HP Constant Torque)

037 - Applicable Motor Capacity (50 HP Constant Torque)

045 - Applicable Motor Capacity (60 HP Constant Torque)

055 - Applicable Motor Capacity (75 HP Constant Torque)

075 - Applicable Motor Capacity (100 HP Constant Torque)

090 - Applicable Motor Capacity (125 HP Constant Torque)

110 - Applicable Motor Capacity (150 HP Constant Torque)

132 - Applicable Motor Capacity (200 HP Constant Torque)

160 - Applicable Motor Capacity (250 HP Constant Torque)

220 - Applicable Motor Capacity (300 HP Constant Torque)

III	iH - Series name of inverter (inverter H - Series)

*	IV	2 - Represents Input Voltage Rating (200-240 V ac)

4 - Represents Input Voltage Rating (380-480 V ac)

V	U- Indicates UL Listed drive.

VI	DB - Optional - Dynamic Braking Chopper.